|  | WHSMP09 – FOR – 08 Structural Alterations & Penetrations |  |
| --- | --- | --- |

Applies to - All structural alterations and any penetrations through building elements on SCU campuses (NSW and QLD)

This supplement must be used for any work involving structural alteration or penetration that may impact building integrity, building services, waterproofing, fire safety systems, or introduce uncontrolled exposure to hazardous energy or materials.

Applies to - Contractors - SCU staff trades - Minor works contractors engaged through Property Services

STOP WORK RULE

Work must stop immediately if any unexpected condition is identified, including unknown services, suspected asbestos or other hazardous materials, cracking, structural movement, water ingress, or any condition outside the approved scope. Notify the Permit Authority and Property Services. Do not recommence until formally cleared and re-authorised.

| PERMIT DETAILS |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PERMIT HOLDER | WORK SUMMARY AND SCOPE CONTROL |  |  |  |  |  |  |  |  |
|  | Campus - Building - Level _____________________Room/Area: _______________________________ |  |  |  |  |  |  |  |  |
|  | Exact work point - mark-up reference (photo/sketch/drawing No.): _______________________________ |  |  |  |  |  |  |  |  |
|  | Asset/space reference (if applicable): _______________________________ |  |  |  |  |  |  |  |  |
|  | Is area occupied during works? ☐ Yes ☐ No ☐ N/A If Yes - access controls in place (barriers, spotter, scheduling, isolation of area): ____________________________________________________________________________________ |  |  |  |  |  |  |  |  |
|  | WORK TYPE (tick all that apply) |  |  |  |  |  |  |  |  |
|  | ☐ Core drilling ☐ Drilling ☐ Saw cutting ☐ Grinding ☐ Demolition/removal |  |  |  |  |  |  |  |  |
|  | ☐ Wall penetration ☐ Floor/slab penetration ☐ Ceiling penetration ☐ Roof penetration ☐ Façade penetration |  |  |  |  |  |  |  |  |
|  | ☐ Structural alteration (modify/remove): ☐ Wall ☐ Beam ☐ Column ☐ Slab ☐ Lintel ☐ Other: _____________ |  |  |  |  |  |  |  |  |
|  | Method/tools (eg core drill size, saw type): _______________________________ |  |  |  |  |  |  |  |  |
|  | DIMENSIONS AND LIMITS |  |  |  |  |  |  |  |  |
|  | Penetration size (diameter/width x height): _____________ mm Depth (or slab thickness): _____________ mm Number of penetrations: _____________ |  | Planned cut line / extent of removal: _______________________________ Scope boundaries confirmed (what is included): _______________________________ Explicit exclusions confirmed (what is not included): _______________________________ |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK - No structural alteration or penetration proceeds unless this supplement is completed, scope is defined, and Permit Authority approval is confirmed. |  |  |  |  |  |  |  | ☐ Confirmed |
|  | PRE-CHECKS AND APPROVALS |  |  |  |  |  |  |  |  |
|  | PROPERTY SERVICES APPROVAL |  |  |  |  |  |  |  |  |
|  | Property Services approval to proceed obtained ☐ Yes ☐ No - Approval reference / email / job number: _______________________________ - Permit Authority name: _______________________________ Date: //____ |  |  |  |  |  |  |  |  |
|  | DRAWINGS AND AS-BUILT REVIEW |  |  |  |  |  |  |  |  |
|  |  Relevant as-built drawings requested and reviewed - Drawing numbers / documents reviewed: _______________________________ |  |  | ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |
|  |  Service routes and building element type confirmed from documentation ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | ENGINEERING REVIEW - TRIGGERS (tick as applicable) |  |  |  |  |  |  |  |  |
|  | Structural engineer review and written approval is mandatory where any apply: ☐ Load-bearing element impacted or suspected (beam/column/slab/structural wall) ☐ Alteration to structural framing or reinforcement possible ☐ Multiple penetrations in close proximity or large diameter penetrations ☐ Penetration within post-tensioned slab or suspected post-tensioning ☐ Removal of bracing, lintels, or supports ☐ Demolition beyond non-structural finishes ☐ Any uncertainty about structural status |  |  |  |  |  |  |  |  |
|  | Structural engineer engaged and approval received ☐ Yes ☐ No ☐ N/A - Engineer name/company: _______________________________ - Approval reference: _______________________________ |  |  |  |  |  |  |  |  |
|  | FIRE SAFETY REVIEW - TRIGGERS |  |  |  |  |  |  |  |  |
|  | Fire safety review and approval is mandatory where any apply: ☐ Penetration through fire-rated wall/floor/ceiling or fire/smoke compartment boundary ☐ Work impacts fire doors, fire dampers, fire stopping, risers, shafts, plant rooms, egress routes ☐ Work impacts detection, alarms, sprinklers, hydrants, hose reels, smoke control systems Fire safety officer/fire engineer review completed ☐ Yes ☐ No ☐ N/A - Reviewer name: _______________________________ - Approval reference: _______________________________ |  |  |  |  |  |  |  |  |
|  | HERITAGE OR APPROVALS PATHWAY |  |  |  |  |  |  |  |  |
|  | Heritage/DA implications checked with Property Services ☐ Yes ☐ No ☐ N/A Notes/actions: _______________________________ |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK |  |  |  |  |  |  |  |  |
|  | If engineering or fire safety review is triggered, no work proceeds until written approval is provided and attached to the permit pack. |  |  |  |  | ☐ Confirmed |  |  |  |
|  | SERVICE LOCATING AND VERIFICATION OF NO LIVE SERVICES |  |  |  |  |  |  |  |  |
|  | SERVICE INFORMATION SOURCES USED (tick all used) |  |  |  |  |  |  |  |  |
|  | ☐ Dial Before You Dig ☐ As-built drawings ☐ SCU internal services information ☐ Building/area inspection ☐ Consultation with Property Services/SCU maintenance Reference details (DBYD No., drawing Nos., info source): _______________________________ |  |  |  |  |  |  |  |  |
|  | NON-DESTRUCTIVE SCANNING AND VERIFICATION |  |  |  |  |  |  |  |  |
|  | - Service scanning completed where required (GPR, cable locator, ferrous scan) ☐ Yes ☐ No ☐ N/A - Scanning is mandatory where any apply: - ☐ Penetration through slab/wall of unknown construction - ☐ Work within plant rooms, risers, services corridors, wet areas, external façade zones - ☐ Work near known service routes, distribution boards, comms rooms - ☐ Any uncertainty from drawings or inspection - Scan results recorded and attached (mark-up/photo) ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | ISOLATION AND VERIFICATION |  |  |  |  |  |  |  |  |
|  | Is any service isolation required? ☐ Yes ☐ No - Services to isolate (tick) ☐ Electrical ☐ Gas ☐ Hydraulics ☐ Fire services ☐ Comms ☐ Medical gases ☐ Other: ______ - Isolation method (LOTO, valves, permits): _______________________________ - Isolation verified (test before touch where electrical) ☐ Yes ☐ No ☐ N/A - Responsible person (name): _______________________________ |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK - No penetration until services are cleared and authorised by the Permit Authority. Evidence (scan results, drawings, mark-up) must be available on-site. |  |  |  |  | ☐ Confirmed |  |  |  |
|  | HAZARDOUS MATERIALS AND AIRBORNE CONTAMINANT CONTROLS |  |  |  |  |  |  |  |  |
|  | ASBESTOS AND HAZARDOUS MATERIALS CHECKS |  |  |  |  |  |  |  |  |
|  | - Asbestos register checked for the area and attached/available ☐ Yes ☐ No ☐ N/A - If asbestos is identified or suspected - work stops and is managed under asbestos controls ☐ Acknowledged - Other potential hazardous materials assessed (tick as relevant): - ☐ Silica generating materials (concrete, brick, block, engineered stone) - ☐ Lead-based paint - ☐ PCBs (older electrical components, sealants) - ☐ Mould / biological contamination - ☐ Synthetic mineral fibres (MMVF/SMF insulation) - ☐ Other: _______________________________ |  |  |  |  |  |  |  |  |
|  | SILICA AND DUST CONTROLS (if cutting, grinding, drilling, chasing) |  |  |  |  |  |  |  |  |
|  | Primary control method (tick): ☐ Wet cutting/wet drilling ☐ On-tool extraction (HEPA) ☐ Both No dry cutting unless justified and approved by Permit Authority ☐ Confirmed Dust containment (screens, negative air if needed) ☐ Yes ☐ No ☐ N/A Respiratory protection selected and fit checked as required ☐ Yes ☐ No ☐ N/A Clean-up method (tick): ☐ HEPA vacuum ☐ Wet wipe ☐ Other: _____________ Compressed air blow-down prohibited ☐ Confirmed |  |  |  |  |  |  |  |  |
|  | WASTE HANDLING AND DISPOSAL |  |  |  |  |  |  |  |  |
|  | - Waste segregation and containment arranged ☐ Yes ☐ No ☐ N/A - Waste labelled and removed from site appropriately ☐ Yes ☐ No ☐ N/A - Disposal pathway confirmed (including hazardous waste if applicable) ☐ Yes ☐ No ☐ N/A - Notes: _______________________________ |  |  |  |  |  |  |  |  |
|  | AIR MONITORING TRIGGERS |  |  |  |  |  |  |  |  |
|  | - Air monitoring required (tick if applicable): ☐ Asbestos removal ☐ High dust exposure risk ☐ Confined/poorly ventilated area ☐ As directed by Property Services/WHS - If required - monitoring arranged and results managed ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK |  |  |  |  |  |  |  |  |
|  | If any friable material, suspected asbestos, unusual dust/odour, biological contamination, or unknown insulation is identified - stop work and notify Permit Authority and Property Services. |  |  |  |  | ☐ Confirmed |  |  |  |
|  | STRUCTURAL INTEGRITY AND TEMPORARY WORKS |  |  |  |  |  |  |  |  |
|  | STRUCTURAL STATUS CONFIRMATION |  |  |  |  |  |  |  |  |
|  | - Building element type confirmed (tick): ☐ Non-structural partition ☐ Structural wall ☐ Slab ☐ Beam ☐ Column ☐ Lintel ☐ Unknown If unknown - treat as structural and engage engineering review ☐ Acknowledged |  |  |  |  |  |  |  |  |
|  | TEMPORARY WORKS AND STABILITY CONTROLS |  |  |  |  |  |  |  |  |
|  | - Is propping/shoring/temporary support required? ☐ Yes ☐ No ☐ N/A - Temporary works design/approval obtained (if required) ☐ Yes ☐ No ☐ N/A - Competent person responsible: _______________________________ - Exclusion zone established for potential collapse/falling debris ☐ Yes ☐ No ☐ N/A - Falling object controls in place (catch platform, toe boards, debris netting if relevant) ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | LIMITS ON CUTTING AND ALTERATION |  |  |  |  |  |  |  |  |
|  | - No cutting of reinforcement or structural members unless engineered and approved ☐ Confirmed - No additional penetrations or enlarged penetrations beyond approved scope ☐ Confirmed - Maximum allowable penetration parameters confirmed (per engineer or Property Services) ☐ Yes ☐ No ☐ N/A - Details: _______________________________ |  |  |  |  |  |  |  |  |
|  | POST-WORK INSPECTION |  |  |  |  |  |  |  |  |
|  | - Structural area inspection required after works ☐ Yes ☐ No ☐ N/A - Inspection completed by (name/role): _______________________________ Date: //____ Findings/actions: _______________________________ |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK - Before altering any load-bearing element, written structural engineer approval must be provided and verified on-site. |  |  |  |  |  | ☐ Confirmed |  |  |
|  | FIRE AND SMOKE COMPARTMENTATION - FIRE STOPPING AND REINSTATEMENT |  |  |  |  |  |  |  |  |
|  | Fire-rated element identification |  |  |  |  |  |  |  |  |
|  | - Is the penetration through a fire-rated element or compartment boundary? ☐ Yes ☐ No ☐ Unknown - If Unknown - treat as fire-rated until confirmed by Property Services ☐ Acknowledged - Element type (tick): ☐ Wall ☐ Floor/slab ☐ Ceiling ☐ Shaft/riser ☐ Plant room boundary - ☐ Other: _____________ |  |  |  |  |  |  |  |  |
|  | FIRE STOPPING AND SEALING REQUIREMENTS |  |  |  |  |  |  |  |  |
|  | - Fire stopping system selected is suitable for the element, service type, and rating ☐ Yes ☐ No ☐ N/A - Fire stopping product/system details (manufacturer/system ID): _______________________________ - Installation by competent person (name/company): _______________________________ - Fire stopping installed as per system requirements (no substitutions) ☐ Confirmed |  |  |  |  |  |  |  |  |
|  | FIRE SYSTEMS IMPAIRMENT AND TEMPORARY CONTROLS |  |  |  |  |  |  |  |  |
|  | - Are fire systems impacted (detection/sprinklers/alarms)? ☐ Yes ☐ No - If Yes - impairment controls implemented and approved by Property Services ☐ Yes ☐ No ☐ N/A Temporary controls (fire watch, isolation approval, reinstatement plan): _______________________________ |  |  |  |  |  |  |  |  |
|  | EVIDENCE AND REINSTATEMENT |  |  |  |  |  |  |  |  |
|  | - Photos taken pre and post fire stopping ☐ Yes ☐ No ☐ N/A - Product data/certification provided where required ☐ Yes ☐ No ☐ N/A - Fire integrity reinstated prior to handback ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK |  |  |  |  |  |  |  |  |
|  | HOLD POINT - STOP WORK - Area must not be handed back until fire integrity is fully reinstated and evidence is provided to Property Services. |  |  |  |  |  |  | ☐ Confirmed |  |
|  | UTILITIES, ISOLATIONS, AND ENERGY CONTROL |  |  |  |  |  |  |  |  |
|  | ELECTRICAL SAFETY |  |  |  |  |  |  |  |  |
|  | - Electrical hazards assessed and controlled ☐ Yes ☐ No ☐ N/A - RCD protection in place for portable tools ☐ Yes ☐ No ☐ N/A - Test before touch applied where electrical exposure is possible ☐ Yes ☐ No ☐ N/A - Electrical permit interface required (if applicable) ☐ Yes ☐ No ☐ N/A - Reference: _______________________________ |  |  |  |  |  |  |  |  |
|  | OTHER UTILITIES |  |  |  |  |  |  |  |  |
|  | - Gas isolation verified where required ☐ Yes ☐ No ☐ N/A - Hydraulics isolation verified where required ☐ Yes ☐ No ☐ N/A - Comms/critical services impacts managed with Property Services ☐ Yes ☐ No ☐ N/A - Medical gases (if applicable) isolated and verified by authorised person ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | DUST IGNITION AND FIRE RISK (where applicable) |  |  |  |  |  |  |  |  |
|  | - Ignition sources controlled where combustible dust risk exists ☐ Yes ☐ No ☐ N/A - Hot work involved? ☐ Yes ☐ No - If Yes - Hot Work permit requirements applied and attached ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | SITE CONTROLS AND PUBLIC PROTECTION |  |  |  |  |  |  |  |  |
|  | ACCESS CONTROL AND BARRICADING |  |  |  |  |  |  |  |  |
|  | - Barricades and signage installed ☐ Yes ☐ No ☐ N/A - Exclusion zone defined and maintained ☐ Yes ☐ No ☐ N/A - Spotter required due to public interface or overhead hazards ☐ Yes ☐ No ☐ N/A Spotter name: _______________________________ |  |  |  |  |  |  |  |  |
|  | NOISE, VIBRATION, AND SCHEDULING |  |  |  |  |  |  |  |  |
|  | - Noise and vibration controls implemented ☐ Yes ☐ No ☐ N/A - Out-of-hours approval required and obtained ☐ Yes ☐ No ☐ N/A Approval reference: _______________________________ |  |  |  |  |  |  |  |  |
|  | EMERGENCY ARRANGEMENTS |  |  |  |  |  |  |  |  |
|  | - Emergency exits, alarms, and egress routes maintained ☐ Yes ☐ No ☐ N/A - First aid arrangements confirmed ☐ Yes ☐ No ☐ N/A - Emergency contacts available on-site ☐ Yes ☐ No ☐ N/A If fire protection impaired - additional emergency controls implemented ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | COMPETENCY AND DOCUMENTATION PACK |  |  |  |  |  |  |  |  |
|  | SWMS AND HIGH RISK CONSTRUCTION WORK |  |  |  |  |  |  |  |  |
|  | Does the work trigger high risk construction work? ☐ Yes ☐ No ☐ Unsure If Yes - SWMS must be provided, briefed, and available on-site. ☐ Confirmed Trigger checklist (tick if applicable): ☐ Risk of fall >2 m ☐ Demolition or structural alteration | ☐ Penetration through load-bearing element ☐ Work near energised electrical installations or services ☐ Use of powered mobile plant in exclusion zones ☐ Work in or near confined space entry points/shafts/risers ☐ Work involving silica generating activities ☐ Other site-specific triggers: _______________________________ |  |  |  |  |  |  |  |
|  | Competency evidence | Plant, tooling, and equipment checks |  |  |  |  |  |  |  |
|  | - Trade qualifications verified ☐ Yes ☐ No ☐ N/A - Relevant licences/tickets (if applicable) verified ☐ Yes ☐ No ☐ N/A - Silica/asbestos awareness where relevant verified ☐ Yes ☐ No ☐ N/A - Supervisor nominated for the task (name): _______________________________ | - Tools inspected and suitable (guards, discs, leads, couplings) ☐ Yes ☐ No ☐ N/A - RCD tested and current ☐ Yes ☐ No ☐ N/A - Dust extraction / wet suppression functional ☐ Yes ☐ No ☐ N/A - PPE available and used (eye, hearing, respiratory, gloves) ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |
|  | Permit interfaces (tick if required and attach) |  |  |  |  |  |  |  |  |
|  | - ☐ Working at Heights PTW supplement - ☐ Hot Work permit - ☐ Confined Space permit | - ☐ Excavation permit - ☐ Electrical access/isolations permit interface - ☐ Other: _______________________________ |  |  |  |  |  |  |  |
|  | Verification, handback, and close-out |  |  |  |  |  |  |  |  |
|  | MAKING SAFE AND CLEAN-UP |  |  |  |  |  |  |  |  |
|  | - Work area cleaned and made safe ☐ Yes ☐ No ☐ N/A - All debris removed - no trip hazards - no sharp edges - penetrations sealed ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | REINSTATEMENT |  |  |  |  |  |  |  |  |
|  | - Fire stopping completed and verified ☐ Yes ☐ No ☐ N/A - Waterproofing reinstated where relevant ☐ Yes ☐ No ☐ N/A - Acoustic/sealing reinstated where relevant ☐ Yes ☐ No ☐ N/A - Finishes reinstated (ceilings, walls, flooring) ☐ Yes ☐ No ☐ N/A |  |  |  |  |  |  |  |  |
|  | POST-WORK VERIFICATION |  |  |  |  |  |  |  |  |
|  | - Services tested and confirmed operational (where impacted) ☐ Yes ☐ No ☐ N/A - Fire systems returned to normal (where impacted) ☐ Yes ☐ No ☐ N/A - Structural area inspected and acceptable (where applicable) ☐ Yes ☐ No ☐ N/A - Evidence submitted to Property Services (tick and describe): - ☐ Photos (pre, during, post) - ☐ Mark-ups / as-built updates - ☐ Fire stopping product data / certification - ☐ Engineer approval / inspection record - ☐ Other: _______________________________ |  |  |  |  |  |  |  |  |
|  | FINAL HANDBACK AUTHORITY |  |  |  |  |  |  |  |  |
|  | - Area is safe for re-occupation and handed back to SCU ☐ Yes ☐ No - Handover notes/defects/outstanding actions: _______________________________ |  |  |  |  |  |  |  |  |

|  | WHSMP09 – FOR – 08 Structural Alterations & Penetrations | Property Services |
| --- | --- | --- |

| PERMIT AUTHORISATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| ISSUER | I, the Permit Issuer, approve this Structural Alteration & Penetration work to proceed and confirm that: ☐ Scope of work has been reviewed and approved ☐ Relevant drawings and service information have been reviewed ☐ Engineering and fire safety approvals have been obtained where required ☐ Hazardous materials and asbestos checks have been completed ☐ Required isolations and service verifications are confirmed ☐ A task-specific Risk Assessment has been completed and reviewed ☐ A SWMS has been prepared where required and briefed to the work team - Name of Permit Issuer: Signature: Date of Issue: |  |  |  |
| PERMIT DECLARATION |  |  |  |  |
| PERMIT HOLDER | As the Permit Holder, I acknowledge and understand the conditions of this permit and: - Declare I am competent to coordinate this work in accordance with this permit and associated risk assessment. - Will implement all the controls highlighted above and outlined in the risk assessment and as specified by the permit authority. - Shall share this permit and associated risk assessment with the other worker/s to ensure they understand the conditions of this permit. - Will immediately cease operations if any of the above conditions cannot be met. Name of Permit Holder: Signature: Date: My signature below acknowledges that I agree and understand the conditions of this permit (other worker/s). Name of worker: _ Signature: Date: Name of worker: _ Signature: Date: Name of worker: _ Signature: Date: |  |
| FINALISATION |  |  |
| PERMIT HOLDER |  | As the Permit Holder, I confirm all work is complete, all workers have signed off the Permit and the worksite has been left clean, tidy and All temporary work controls (barricades, exclusion zones and isolation controls) have been removed and the area has been left safe. Name of Permit Holder: Signature: Date: |  |
| FEEDBACK |  |  |  |
| NON- COMPLIANCE |  |  |  |